## Slide 1: Overview
Chart: Primary Current (A)
| 0.01 | 0.02 | 0.05 | 0.1 | 0.2 | 0.5 | 1 | 2 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
1,000 Ω | 3.343 | 6.403 | 16.567 | 33.095 | 66.2312 | 165.78 | 329.866 | 659.6714 | 1649.633 | 3279.773 | 4880.825 | 6153.93 | 6330.074 | 6315.631
100 Ω | 0.333 | 0.6919 | 1.722 | 3.343 | 6.6824 | 16.668 | 33.2694 | 66.6701 | 167.0237 | 332.5223 | 498.435 | 663.9942 | 829.5938 | 994.3551 | 1157.662 | 1325.928 | 1486.215 | 1628.322 | 1720.939 | 1797.396
50 Ω | 0.22 | 0.33 | 0.856 | 1.718 | 3.3359 | 8.347 | 16.665 | 33.3502 | 83.3755 | 166.7308 | 249.672 | 332.593 | 415.2413 | 497.6876 | 579.8713 | 662.7115 | 744.0468 | 823.655 | 886.1336 | 937.987
10 Ω | 0.1533 | 0.16 | 0.203 | 0.332 | 0.7096 | 1.7225 | 3.381 | 6.722 | 16.767 | 33.51 | 50.208 | 66.883 | 83.616 | 100.259 | 116.95 | 133.91 | 150.45 | 166.79 | 182.84 | 194.92
The C/CT series are clamp-on current sensors that can be used to measure currents in live wires. C/CT-0306 is suitable for currents from 10 up to 30 A.
Benefits
Compact and slim design
Flat temperature characteristics
UL 94 V–0 flame retardant rated case
RoHS compliant
C/CT Series
Applications
EMS current measurement
High performance distributions boards
Power conditioners
Power monitoring systems
Inverters
Industrial machinery
https://www.kemet.com/en/us/sensors
C/CT Series, High Current AC Sensor, Snap-on Type
C/CT-0306
Electrical Characteristics
Item | Performance Characteristics
Rated Current | 30 A for C/CT-0306
 | 80 A for C/CT-0810
 | 120 A for C/CT-1216
 | 250 A for C/CT-2524
Applicable Current | 0.1 – 50 A for C/CT-0306
 | 0.1 – 120 A for C/CT-0810
 | 0.1 – 150 A for C/CT-1216
 | 0.1 – 340 A for C/CT-2524
Output Voltage | 100 ±2 mV for C/CT-0306
 | 270 ±5 mV for C/CT-0810
 | 400 ±8 mV for C/CT-1216
 | 1,250 ±25 mV for C/CT-2524
Current Transformation Ratio | 3,000 for C/CT-0306, C/CT-0810 and C/CT-1216
 | 2,000 for C/CT-2524
Output Protection | 7.5 V
Insulation Resistance | 100 MΩ at 500 VDC
Operating Temperature Range | -10ºC to +60ºC
Storage Temperature Range | -20ºC to +75ºC
Output Voltage
C/CT-1216
C/CT-2524
C/CT-0810

## Slide 2: Overview
Chart: 
| 0.1 | 0.15 | 0.3 | 1.5 | 3 | 6 | 15 | 30 | 45 | 60 | 81 | 90 | 99 | 108 | 119 | 130
1,000 Ω | 35.988 | 53.452 | 104.9 | 499.55 | 996.4 | 1983.9 | 4982.3 | 7031.9 | 7482.4 | 7705.1 | 7561.5 | 7414.9
100 Ω | 3.711 | 5.37 | 10.616 | 50.36 | 100.455 | 199.99 | 503.55 | 995.63 | 1498.2 | 1996.5 | 2693.4 | 2990.2 | 3285.7 | 3576 | 3785 | 3977.1
50 Ω | 1.822 | 2.697 | 5.3119 | 25.202 | 50.213 | 100.2 | 249.6 | 500.63 | 749.13 | 998.8 | 1346.5 | 1494.4 | 1644.3 | 1792.2 | 1962.2 | 2098.1
10 Ω | 0.424 | 0.6005 | 1.0981 | 5.0522 | 10.045 | 19.984 | 50.115 | 99.888 | 149.86 | 199.7 | 269.45 | 299.41 | 329.03 | 359.03 | 393.97 | 428.44
The C/CT series are clamp-on current sensors that can be used to measure currents in live wires. C/CT-0810 is suitable for currents from 50 up to 80 A.
Benefits
Compact and slim design
Flat temperature characteristics
UL 94 V–0 flame retardant rated case
RoHS compliant
C/CT Series
Applications
EMS current measurement
High performance distributions boards
Power conditioners
Power monitoring systems
Inverters
Industrial machinery
https://www.kemet.com/en/us/sensors
C/CT Series, High Current AC Sensor, Snap-on Type
C/CT-0810
C/CT-1216
C/CT-2524
Electrical Characteristics
Item | Performance Characteristics
Rated Current | 30 A for C/CT-0306
 | 80 A for C/CT-0810
 | 120 A for C/CT-1216
 | 250 A for C/CT-2524
Applicable Current | 0.1 – 50 A for C/CT-0306
 | 0.1 – 120 A for C/CT-0810
 | 0.1 – 150 A for C/CT-1216
 | 0.1 – 340 A for C/CT-2524
Output Voltage | 100 ±2 mV for C/CT-0306
 | 270 ±5 mV for C/CT-0810
 | 400 ±8 mV for C/CT-1216
 | 1,250 ±25 mV for C/CT-2524
Current Transformation Ratio | 3,000 for C/CT-0810, C/CT-0306 and C/CT-1216
 | 2,000 for C/CT-2524
Output Protection | 7.5 V
Insulation Resistance | 100 MΩ at 500 VDC
Operating Temperature Range | -10ºC to +60ºC
Storage Temperature Range | -20ºC to +75ºC
Output Voltage
C/CT-0306

## Slide 3: Overview
The C/CT series are clamp-on current sensors that can be used to measure currents in live wires. C/CT-1216 is suitable for currents from 100 up to 120 A.
.
Benefits
Compact and slim design
Flat temperature characteristics
UL 94 V–0 flame retardant rated case
RoHS compliant
C/CT Series
Applications
EMS current measurement
High performance distributions boards
Power conditioners
Power monitoring systems
Inverters
Industrial machinery
C/CT Series, High Current AC Sensor, Snap-on Type
C/CT-1216
Electrical Characteristics
Output Voltage
Item | Performance Characteristics
Rated Current | 30 A for C/CT-0306
 | 80 A for C/CT-0810
 | 120 A for C/CT-1216
 | 250 A for C/CT-2524
Applicable Current | 0.1 – 50 A for C/CT-0306
 | 0.1 – 120 A for C/CT-0810
 | 0.1 – 150 A for C/CT-1216
 | 0.1 – 340 A for C/CT-2524
Output Voltage | 100 ±2 mV for C/CT-0306
 | 270 ±5 mV for C/CT-0810
 | 400 ±8 mV for C/CT-1216
 | 1,250 ±25 mV for C/CT-2524
Current Transformation Ratio | 3,000 for C/CT-1216, C/CT-0306 and C/CT-0810
 | 2,000 for C/CT-2524
Output Protection | 7.5 V
Insulation Resistance | 100 MΩ at 500 VDC
Operating Temperature Range | -10ºC to +60ºC
Storage Temperature Range | -20ºC to +75ºC
Chart: 
| 0.1 | 0.5 | 1 | 3 | 5 | 8 | 9 | 10 | 15 | 30 | 50 | 80 | 90 | 100 | 120 | 130 | 140 | 150 | 160 | 180 | 200 | 240
1,000 Ω | 33.21 | 166.73 | 331.2 | 992.6 | 1655.5 | 2663 | 2987 | 3331 | 4977 | 7345 | 8102 | 8558 | 8648 | 8713 | 8826
100 Ω | 3.29 | 16.66 | 33.07 | 99.57 | 166.24 | 332.9 | 498.9 | 997.7 | 1661.9 | 3349 | 4001 | 4333 | 4661 | 4997 | 5327 | 5943 | 6358 | 6653
60 Ω | 2 | 9.92 | 19.77 | 59.65 | 99.71 | 199.8 | 299.4 | 598.4 | 999.6 | 2025 | 2414 | 2609 | 2806 | 3005 | 3205 | 3601 | 3989 | 4760
10 Ω | 1.7 | 3.26 | 9.86 | 16.55 | 33.25 | 49.89 | 99.7 | 166.89 | 334.2 | 400.3 | 433.2 | 466.2 | 499.6 | 532.4 | 597.5 | 663.6 | 795.7
C/CT-0810
C/CT-2524
C/CT-0306
©KEMET Corporation. All Rights Reserved.
https://www.kemet.com/en/us/sensors

## Slide 4: Overview
Chart: 
| 0.01 | 1 | 2 | 18 | 60 | 99 | 150 | 180 | 250 | 265 | 285 | 300 | 312 | 330 | 352 | 374 | 396 | 418 | 440
100 Ω | 50.072 | 99.72 | 895.95 | 3004.5 | 4959.8 | 6655 | 7062 | 7633 | 7671 | 7653 | 7645
50 Ω | 25.0333 | 49.9942 | 448.7833 | 1512.25 | 2496.75 | 3781.75 | 4534.3333 | 5571.6667 | 5665.6667 | 5720.8333 | 5775 | 5779.4167
10 Ω | 4.93 | 9.97 | 90.3 | 301 | 496.8 | 752.6 | 903.3 | 1253.3 | 1501 | 1740.5 | 1818.9 | 1892.7 | 1966 | 2029
The C/CT series are clamp-on current sensors that can be used to measure currents in live wires. C/CT-2524 is suitable for currents from 200 up to 250 A.
.
Benefits
Compact and slim design
Flat temperature characteristics
UL 94 V–0 flame retardant rated case
RoHS compliant
C/CT Series
Applications
EMS current measurement
High performance distributions boards
Power conditioners
Power monitoring systems
Inverters
Industrial machinery
C/CT Series, High Current AC Sensor, Snap-on Type
C/CT-2524
Electrical Characteristics
Output Voltage
Item | Performance Characteristics
Rated Current | 30 A for C/CT-0306
 | 80 A for C/CT-0810
 | 120 A for C/CT-1216
 | 250 A for C/CT-2524
Applicable Current | 0.1 – 50 A for C/CT-0306
 | 0.1 – 120 A for C/CT-0810
 | 0.1 – 150 A for C/CT-1216
 | 0.1 – 340 A for C/CT-2524
Output Voltage | 100 ±2 mV for C/CT-0306
 | 270 ±5 mV for C/CT-0810
 | 400 ±8 mV for C/CT-1216
 | 1,250 ±25 mV for C/CT-2524
Current Transformation Ratio | 3,000 for C/CT-0306, C/CT-0810 and C/CT-1216
 | 2,000 for C/CT-2524
Output Protection | 7.5 V
Insulation Resistance | 100 MΩ at 500 VDC
Operating Temperature Range | -10ºC to +60ºC
Storage Temperature Range | -20ºC to +75ºC
C/CT-0810
C/CT-1216
C/CT-0306
©KEMET Corporation. All Rights Reserved.
https://www.kemet.com/en/us/sensors